## Acoustic Louvre System
COPY -------------------------------------------------------------------------------------------------- COPY
Acoustic Louvre System
System Manufacturer
Caice Acoustic Air Movement Ltd
Riverside House, 3 Winnersh Fields
Gazelle Close, Winnersh
Berkshire RG41 5QS
T: 0118-918-6470 E: enquiries@caice.co.uk www.caice.co.uk
Select the Manufacturer's Scope of work:
System Outline
Fabricated Acoustic Louvre system manufactured from galvanised sheet steel as standard.
Louvre blades of 1.0mm thick galvanised steel, filled with high density mineral wool acoustic
media, retained behind fibre glass tissue and XPM perforated galvanised sheet steel on the
underside of the blade. Module outer casing 1.2mm thick galvanised steel.
Bird guard where fitted to be manufactured from XPM perforated 304 stainless steel.
Select the Acoustic Louvre System framing:
Double leaf door - emergency exit (CE marked)
Select the Polyester Powder Coating requirement:
RAL/BS - ** | Edit the level of gloss required:
Acoustic Performance
dB in each Octave Band Centre Frequency (Hz)
Sound Reduction Index 63 125 250 500 1k 2k 4k 8k Rw
SH300 Acoustic Louvre panel 300mm deep 7 7 10 17 29 30 27 21 21
COPY -------------------------------------------------------------------------------------------------- COPY

## Sheet2
Select the Manufacturer's Scope of work:
Manufacturer's scope of work - Supply and Install
Manufacturer's scope of work - Supply Only
Select the Polyester Powder Coating requirement:
Polyester powder coating. Individual component parts coated, prior to factory assembly of modules.
Plain galvanised steel finish
Edit the level of gloss required:
Level of gloss - Matt (typically 25 % +/-10%)
Level of gloss - Satin (typically 65 % +/-10%)
Level of gloss - Gloss (typically 85 % +/-10%)
Select the acoustic performance required for the Acoustic Louvre System:
SS150 Acoustic Louvre panel 150mm deep 4 4 6 8 11 11 11 10 11
SH150 Acoustic Louvre panel 150mm deep 5 5 7 9 13 13 13 12 13
SS300 Acoustic Louvre panel 300mm deep 6 6 9 13 21 20 16 16 17
SH300 Acoustic Louvre panel 300mm deep 7 7 10 17 29 30 27 21 21
CS300 Acoustic Louvre panel 300mm deep 5 6 8 12 19 19 18 17 16
CS600 Acoustic Louvre panel 600mm deep 7 8 13 23 37 33 29 29 25
Select the required CE marked doorset if required:
Single leaf door - emergency exit (CE marked)
Double leaf door - emergency exit (CE marked)
Single leaf door - non escape route (CE marked)
Double leaf door - non escape route (CE marked)
Not required
Select the Acoustic Louvre System framing:
Continuous Line, frameless front face appearance
Front face framed, modular sections