## Sheet
Fan Coil Unit Technical Schedule | [34 empty] | Schedule Date
2024-03-18
Manchester Airport T2 Mag T2r Fcus | [34 empty] | Caice Reference
122835/Q00018
MANTPT2R-MAN.TL2.XX.XX-HLE-H-SH-HVAC-0008 Rev V3.0
Revised to remove Traffolyte Labels
Notes
All fan coil units as supplied by Caice, as per their file reference , contact the Caice sales team on enquiries@caice.co.uk or call 0118 918 6470.
Fan coil unit technical data is published in accordance with the following standards: BS EN ISO 3741:2010, BS 4856-4:1997, BS EN 1397:2015 and BS 8850:2020.
* Air off temperatures are for guidance purposes only as BS EN 1397:2015 does not specify measurement of this data.
Fan Coil Units
Product Reference | Product Code | Dimensions (mm) |  |  |  | Weight (kg) | Inlet Attenuator (mm) | Discharge Attenuator (mm) | Noise Level Room 1 | Noise Level Room 2 | Air Volume (l/s) | External Pressure (Pa) | Cooling | [13 empty] | Heating | [9 empty] | Control Voltage (V) | SFP (W/l/s) | Minimum Spigots Required | Qty
|  | Width |  | Height | Overall Length | [7 empty] | Medium | Sens. Duty (kW) | Total Duty (kW) | SHR | Air On Dry Bulb (°C) | Air On Wet Bulb (°C) | Air Off Dry Bulb (°C) | Air Off Wet Bulb (°C) | Fluid Flow Rate (l/s) | Fluid Flow Temp (°C) | Fluid Return Temp (°C) | Fluid Pres. Loss (kPa) | Fluid Glycol % | Cond. Rate (kg/h) | Medium | Total Duty (kW) | Air On Dry Bulb (°C) | Air Off Dry Bulb (°C) | Fluid Flow Rate (l/s) | Fluid Flow Temp (°C) | Fluid Return Temp (°C) | Fluid Pres. Loss (kPa) |  | Fluid Glycol %
FCU-00-3001 | FC/H270B/B4/GUW/001SN/----20/2 | 646 |  | 270 | 880 | 34 | None | None | NR 33 |  | 140 | 30 | CHW | 1.32 | 1.32 | 1 | 23 | 16.1 | 16 | 14.7 | 0.045 | 7 | 14 | 3.49 | 0 | 0 | LPHW | 0.52 | 21 | 24.1 | 0.006 | 80 | 60 | 0.1 |  | 0 | 6.79 | 0.22 | 2 | 1
FCU-00-3002 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 30 |  | 217 | 30 | CHW | 1.97 | 2 | 0.99 | 23 | 16.1 | 16 | 15 | 0.068 | 7 | 14 | 3.74 | 0 | 0.04 | LPHW | 0.55 | 21 | 23.1 | 0.007 | 80 | 60 | 0.14 |  | 0 | 5.77 | 0.19 | 3 | 1
FCU-00-3003 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 33 |  | 70 | 30 | CHW | 0.52 | 0.52 | 1 | 23 | 16.1 | 18.7 | 15.7 | 0.018 | 7 | 14 | 1.12 | 0 | 0 | LPHW | 0.23 | 21 | 23.6 | 0.002 | 80 | 60 | 0.1 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3004 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 34 |  | 70 | 30 | CHW | 0.44 | 0.44 | 1 | 23 | 16.1 | 19.6 | 16.3 | 0.015 | 7 | 14 | 0.94 | 0 | 0 | LPHW | 0.13 | 21 | 22.6 | 0.001 | 80 | 60 | 0.04 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3005 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 33 |  | 70 | 30 | CHW | 0.55 | 0.55 | 1 | 23 | 16.1 | 18.3 | 15.4 | 0.019 | 7 | 14 | 1.19 | 0 | 0 | LPHW | 0.2 | 21 | 23.4 | 0.002 | 80 | 60 | 0.08 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3006 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 34 |  | 70 | 30 | CHW | 0.44 | 0.44 | 1 | 23 | 16.1 | 19.6 | 16.3 | 0.015 | 7 | 14 | 0.94 | 0 | 0 | LPHW | 0.16 | 21 | 22.9 | 0.001 | 80 | 60 | 0.06 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3007 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 33 |  | 70 | 30 | CHW | 0.53 | 0.53 | 1 | 23 | 16.1 | 18.5 | 15.5 | 0.018 | 7 | 14 | 1.15 | 0 | 0 | LPHW | 0.18 | 21 | 23.1 | 0.002 | 80 | 60 | 0.07 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3008 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 220 | 30 | CHW | 2.06 | 2.22 | 0.93 | 23 | 16.1 | 16 | 14.7 | 0.076 | 7 | 14 | 3.45 | 0 | 0.23 | LPHW | 0.73 | 21 | 23.8 | 0.009 | 80 | 60 | 0.18 |  | 0 | 6.6 | 0.2 | 3 | 1
FCU-00-3009 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 34 |  | 70 | 30 | CHW | 0.43 | 0.43 | 1 | 23 | 16.1 | 19.7 | 16.3 | 0.015 | 7 | 14 | 0.92 | 0 | 0 | LPHW | 0.11 | 21 | 22.4 | 0.001 | 80 | 60 | 0.03 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3010 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 326 | 30 | CHW | 2.89 | 2.98 | 0.97 | 23 | 16.1 | 16 | 15.1 | 0.102 | 7 | 14 | 4.24 | 0 | 0.13 | LPHW | 0.6 | 21 | 22.5 | 0.007 | 80 | 60 | 0.17 |  | 0 | 5.8 | 0.2 | 4 | 1
FCU-00-3011 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 31 |  | 154 | 30 | CHW | 1.51 | 1.64 | 0.92 | 23 | 16.1 | 16 | 14.5 | 0.056 | 7 | 14 | 2.51 | 0 | 0.19 | LPHW | 0.36 | 21 | 22.9 | 0.004 | 80 | 60 | 0.08 |  | 0 | 5.31 | 0.17 | 2 | 1
FCU-00-3012 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 326 | 30 | CHW | 2.89 | 2.98 | 0.97 | 23 | 16.1 | 16 | 15.1 | 0.102 | 7 | 14 | 4.24 | 0 | 0.13 | LPHW | 0.6 | 21 | 22.5 | 0.007 | 80 | 60 | 0.17 |  | 0 | 5.8 | 0.2 | 4 | 1
FCU-00-3013 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 30 |  | 227 | 30 | CHW | 2.07 | 2.1 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.071 | 7 | 14 | 3.92 | 0 | 0.04 | LPHW | 1.31 | 21 | 25.8 | 0.016 | 80 | 60 | 0.75 |  | 0 | 5.91 | 0.19 | 4 | 1
FCU-00-3014 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 30 |  | 217 | 30 | CHW | 1.97 | 2 | 0.99 | 23 | 16.1 | 16 | 15 | 0.068 | 7 | 14 | 3.74 | 0 | 0.04 | LPHW | 0.55 | 21 | 23.1 | 0.007 | 80 | 60 | 0.14 |  | 0 | 5.77 | 0.19 | 3 | 1
FCU-00-3015 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 33 |  | 70 | 30 | CHW | 0.5 | 0.5 | 1 | 23 | 16.1 | 18.9 | 15.8 | 0.017 | 7 | 14 | 1.08 | 0 | 0 | LPHW | 0.12 | 21 | 22.3 | 0.001 | 80 | 60 | 0.04 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-00-3016 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 30 |  | 227 | 30 | CHW | 2.07 | 2.1 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.071 | 7 | 14 | 3.92 | 0 | 0.04 | LPHW | 1.31 | 21 | 25.8 | 0.016 | 80 | 60 | 0.75 |  | 0 | 5.91 | 0.19 | 4 | 1
FCU-00-3017 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 330 | 30 | CHW | 2.63 | 2.73 | 0.96 | 23 | 16.1 | 16.8 | 15.9 | 0.093 | 7 | 14 | 3.87 | 0 | 0.14 | LPHW | 1.98 | 21 | 26 | 0.024 | 80 | 60 | 1.76 |  | 0 | 5.84 | 0.2 | 4 | 1
FCU-00-3018 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 330 | 30 | CHW | 2.63 | 2.73 | 0.96 | 23 | 16.1 | 16.8 | 15.9 | 0.093 | 7 | 14 | 3.87 | 0 | 0.14 | LPHW | 1.98 | 21 | 26 | 0.024 | 80 | 60 | 1.76 |  | 0 | 5.84 | 0.2 | 4 | 1
FCU-00-3021 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 330 | 30 | CHW | 2.63 | 2.73 | 0.96 | 23 | 16.1 | 16.8 | 15.9 | 0.093 | 7 | 14 | 3.87 | 0 | 0.14 | LPHW | 1.98 | 21 | 26 | 0.024 | 80 | 60 | 1.76 |  | 0 | 5.84 | 0.2 | 4 | 1
FCU-00-3022 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 330 | 30 | CHW | 2.63 | 2.73 | 0.96 | 23 | 16.1 | 16.8 | 15.9 | 0.093 | 7 | 14 | 3.87 | 0 | 0.14 | LPHW | 1.98 | 21 | 26 | 0.024 | 80 | 60 | 1.76 |  | 0 | 5.84 | 0.2 | 4 | 1
FCU-00-3023 | FC/H235H/B4/GUW/001SN/----20/2 | 1591 |  | 235 | 755 | 64 | None | None | NR 32 |  | 276 | 30 | CHW | 2.49 | 2.79 | 0.89 | 23 | 16.1 | 16 | 15.1 | 0.095 | 7 | 14 | 3.54 | 0 | 0.43 | LPHW | 1.5 | 21 | 25.5 | 0.018 | 80 | 60 | 0.59 |  | 0 | 5.77 | 0.17 | 4 | 1
FCU-10-3012 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 34 |  | 227 | 30 | CHW | 1.99 | 2.14 | 0.93 | 23 | 16.1 | 16.4 | 15 | 0.073 | 7 | 14 | 3.31 | 0 | 0.21 | LPHW | 1.36 | 21 | 26 | 0.016 | 80 | 60 | 0.74 |  | 0 | 6.73 | 0.21 | 3 | 1
FCU-10-3026 | FC/H270B/B4/GUW/001SN/----20/2 | 646 |  | 270 | 880 | 34 | None | None | NR 33 |  | 138 | 30 | CHW | 1.3 | 1.3 | 1 | 23 | 16.1 | 16 | 14.7 | 0.045 | 7 | 14 | 3.43 | 0 | 0 | LPHW | 0.54 | 21 | 24.3 | 0.007 | 80 | 60 | 0.11 |  | 0 | 6.72 | 0.22 | 2 | 1
FCU-10-3027 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 32 |  | 139 | 30 | CHW | 1.25 | 1.38 | 0.91 | 23 | 16.1 | 16.8 | 15.1 | 0.047 | 7 | 14 | 2.1 | 0 | 0.19 | LPHW | 0.52 | 21 | 24.1 | 0.006 | 80 | 60 | 0.12 |  | 0 | 5.02 | 0.17 | 2 | 1
FCU-20-3001 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 200 | 30 | CHW | 1.88 | 2.02 | 0.93 | 23 | 16.1 | 16 | 14.6 | 0.069 | 7 | 14 | 3.12 | 0 | 0.2 | LPHW | 0.37 | 21 | 22.5 | 0.004 | 80 | 60 | 0.09 |  | 0 | 6.2 | 0.19 | 3 | 1
FCU-20-3002 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 31 |  | 237 | 30 | CHW | 2.14 | 2.17 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.074 | 7 | 14 | 4.07 | 0 | 0.04 | LPHW | 0.13 | 21 | 22.8 | 0.002 | 80 | 60 | 0.13 |  | 0 | 6.05 | 0.2 | 3 | 1
FCU-20-3003 | FC/H235E/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 51 | None | None | NR 33 |  | 235 | 30 | CHW | 2.19 | 2.4 | 0.91 | 23 | 16.1 | 16 | 14.9 | 0.082 | 7 | 14 | 3.6 | 0 | 0.3 | LPHW | 0.45 | 21 | 22.6 | 0.005 | 80 | 60 | 0.13 |  | 0 | 6.8 | 0.19 | 3 | 1
FCU-20-3004 | FC/H235A/C3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 70 | 30 | CHW | 0.47 | 0.47 | 1 | 23 | 16.1 | 19.2 | 16 | 0.016 | 7 | 14 | 1.01 | 0 | 0 | LPHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-20-3005 | FC/H235A/C3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 70 | 30 | CHW | 0.46 | 0.46 | 1 | 23 | 16.1 | 19.3 | 16.1 | 0.016 | 7 | 14 | 0.99 | 0 | 0 | LPHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-20-3006 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 34 |  | 180 | 30 | CHW | 1.19 | 1.32 | 0.9 | 23 | 16.1 | 18.5 | 16.7 | 0.045 | 7 | 14 | 2 | 0 | 0.18 | LPHW | 1.08 | 21 | 26 | 0.013 | 80 | 60 | 0.49 |  | 0 | 5.82 | 0.18 | 2 | 1
FCU-20-3007 | FC/H235F/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 56 | None | None | NR 32 |  | 240 | 30 | CHW | 2.21 | 2.47 | 0.89 | 23 | 16.1 | 16 | 15 | 0.084 | 7 | 14 | 3.69 | 0 | 0.36 | LPHW | 0.27 | 21 | 21.9 | 0.003 | 80 | 60 | 0.07 |  | 0 | 5.51 | 0.18 | 3 | 1
FCU-20-3008 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 32 |  | 139 | 30 | CHW | 1.28 | 1.41 | 0.91 | 23 | 16.1 | 16.6 | 15 | 0.048 | 7 | 14 | 2.14 | 0 | 0.19 | LPHW | 0.27 | 21 | 22.6 | 0.003 | 80 | 60 | 0.06 |  | 0 | 5.02 | 0.17 | 2 | 1
FCU-20-3009 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 94 | 30 | CHW | 0.81 | 0.81 | 1 | 23 | 16.1 | 17.1 | 14.7 | 0.028 | 7 | 14 | 1.82 | 0 | 0 | LPHW | 0.34 | 21 | 24 | 0.004 | 80 | 60 | 0.16 |  | 0 | 6.05 | 0.2 | 2 | 1
FCU-20-3010 | FC/H235D/C4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 215 | 30 | CHW | 2.01 | 2.16 | 0.93 | 23 | 16.1 | 16 | 14.7 | 0.074 | 7 | 14 | 3.35 | 0 | 0.22 | LPHW | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 6.51 | 0.2 | 3 | 1
FCU-20-3011 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 74 | 30 | CHW | 0.7 | 0.7 | 1 | 23 | 16.1 | 16.8 | 14.3 | 0.024 | 7 | 14 | 1.55 | 0 | 0 | LPHW | 0.17 | 21 | 23 | 0.001 | 80 | 60 | 0.06 |  | 0 | 5.21 | 0.18 | 1 | 1
FCU-20-3012 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 31 |  | 238 | 30 | CHW | 2.16 | 2.19 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.075 | 7 | 14 | 4.1 | 0 | 0.04 | LPHW | 0.35 | 21 | 22.2 | 0.004 | 80 | 60 | 0.09 |  | 0 | 6.06 | 0.2 | 3 | 1
FCU-20-3013 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 33 |  | 104 | 30 | CHW | 0.86 | 0.86 | 1 | 23 | 16.1 | 17.2 | 14.9 | 0.03 | 7 | 14 | 1.95 | 0 | 0 | LPHW | 0.29 | 21 | 23.3 | 0.003 | 80 | 60 | 0.13 |  | 0 | 6.54 | 0.23 | 2 | 1
FCU-20-3014 | FC/H235B/B4/GUW/001SN/----20/2 | 646 |  | 235 | 755 | 31 | None | None | NR 34 |  | 116 | 30 | CHW | 1.19 | 1.21 | 0.98 | 23 | 16.1 | 16 | 14 | 0.041 | 7 | 14 | 2.89 | 0 | 0.03 | LPHW | 0.32 | 21 | 23.3 | 0.004 | 80 | 60 | 0.06 |  | 0 | 6.81 | 0.2 | 2 | 1
FCU-20-3015 | FC/H235B/B4/GUW/001SN/----20/2 | 646 |  | 235 | 755 | 31 | None | None | NR 34 |  | 114 | 30 | CHW | 1.17 | 1.19 | 0.98 | 23 | 16.1 | 16 | 14 | 0.041 | 7 | 14 | 2.84 | 0 | 0.03 | LPHW | 0.38 | 21 | 23.9 | 0.005 | 80 | 60 | 0.07 |  | 0 | 6.73 | 0.2 | 2 | 1
FCU-20-3016 | FC/H235B/B4/GUW/001SN/----20/2 | 646 |  | 235 | 755 | 31 | None | None | NR 32 |  | 102 | 30 | CHW | 1.06 | 1.09 | 0.97 | 23 | 16.1 | 16 | 14 | 0.037 | 7 | 14 | 2.58 | 0 | 0.04 | LPHW | 0.18 | 21 | 22.4 | 0.002 | 80 | 60 | 0.03 |  | 0 | 6.22 | 0.18 | 2 | 1
FCU-20-3017 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 33 |  | 275 | 30 | CHW | 2.45 | 2.49 | 0.98 | 23 | 16.1 | 16 | 15 | 0.085 | 7 | 14 | 4.71 | 0 | 0.06 | LPHW | 0.56 | 21 | 22.7 | 0.007 | 80 | 60 | 0.15 |  | 0 | 6.72 | 0.22 | 4 | 1
FCU-20-3018 | FC/H235F/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 56 | None | None | NR 33 |  | 267 | 30 | CHW | 2.43 | 2.7 | 0.9 | 23 | 16.1 | 16 | 15 | 0.092 | 7 | 14 | 4.05 | 0 | 0.38 | LPHW | 0.75 | 21 | 23.4 | 0.009 | 80 | 60 | 0.21 |  | 0 | 5.89 | 0.19 | 3 | 1
FCU-20-3019 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 215 | 30 | CHW | 2.01 | 2.16 | 0.93 | 23 | 16.1 | 16 | 14.7 | 0.074 | 7 | 14 | 3.35 | 0 | 0.22 | LPHW | 0.24 | 21 | 21.9 | 0.003 | 80 | 60 | 0.05 |  | 0 | 6.51 | 0.2 | 3 | 1
FCU-20-3020 | FC/H235B/B4/GUW/001SN/----20/2 | 646 |  | 235 | 755 | 31 | None | None | NR 32 |  | 101 | 30 | CHW | 1.05 | 1.08 | 0.97 | 23 | 16.1 | 16 | 14 | 0.037 | 7 | 14 | 2.56 | 0 | 0.04 | LPHW | 0.32 | 21 | 23.6 | 0.004 | 80 | 60 | 0.06 |  | 0 | 6.18 | 0.18 | 2 | 1
FCU-20-3021 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 70 | 30 | CHW | 0.67 | 0.67 | 1 | 23 | 16.1 | 16.9 | 14.3 | 0.023 | 7 | 14 | 1.48 | 0 | 0 | LPHW | 0.33 | 21 | 24.9 | 0.003 | 80 | 60 | 0.16 |  | 0 | 5.04 | 0.17 | 1 | 1
FCU-20-3022 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 90 | 30 | CHW | 0.79 | 0.79 | 1 | 23 | 16.1 | 17 | 14.6 | 0.027 | 7 | 14 | 1.77 | 0 | 0 | LPHW | 0.13 | 21 | 22.2 | 0.001 | 80 | 60 | 0.04 |  | 0 | 5.88 | 0.2 | 2 | 1
FCU-20-3024 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 33 |  | 277 | 30 | CHW | 2.48 | 2.53 | 0.98 | 23 | 16.1 | 16 | 14.9 | 0.087 | 7 | 14 | 4.79 | 0 | 0.07 | LPHW | 0.32 | 21 | 22 | 0.004 | 80 | 60 | 0.08 |  | 0 | 6.76 | 0.22 | 4 | 1
FCU-20-3025 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 34 |  | 209 | 30 | CHW | 1.96 | 2.11 | 0.93 | 23 | 16.1 | 16 | 14.7 | 0.072 | 7 | 14 | 3.26 | 0 | 0.21 | LPHW | 0.32 | 21 | 22.3 | 0.004 | 80 | 60 | 0.07 |  | 0 | 6.4 | 0.2 | 3 | 1
FCU-20-3026 | FC/H235F/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 56 | None | None | NR 34 |  | 312 | 30 | CHW | 2.81 | 3.13 | 0.9 | 23 | 16.1 | 16 | 15 | 0.107 | 7 | 14 | 4.73 | 0 | 0.46 | LPHW | 0.17 | 21 | 21.4 | 0.002 | 80 | 60 | 0.04 |  | 0 | 6.62 | 0.22 | 4 | 1
FCU-20-3027 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 34 |  | 227 | 30 | CHW | 2.11 | 2.27 | 0.93 | 23 | 16.1 | 16 | 14.7 | 0.078 | 7 | 14 | 3.53 | 0 | 0.23 | LPHW | 0.43 | 21 | 22.5 | 0.005 | 80 | 60 | 0.1 |  | 0 | 6.73 | 0.21 | 3 | 1
FCU-20-3028 | FC/H235A/B3/GUW/001SN/----20/2 | 430 |  | 235 | 755 | 25 | None | None | NR 32 |  | 71 | 30 | CHW | 0.68 | 0.68 | 1 | 23 | 16.1 | 16.8 | 14.3 | 0.023 | 7 | 14 | 1.5 | 0 | 0 | LPHW | 0.26 | 21 | 24 | 0.003 | 80 | 60 | 0.12 |  | 0 | 5.09 | 0.17 | 1 | 1
FCU-20-3029 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 200 | 30 | CHW | 1.88 | 2.02 | 0.93 | 23 | 16.1 | 16 | 14.6 | 0.069 | 7 | 14 | 3.11 | 0 | 0.2 | LPHW | 0.4 | 21 | 22.6 | 0.005 | 80 | 60 | 0.09 |  | 0 | 6.2 | 0.19 | 3 | 1
FCU-20-3030 | FC/H270K/B4/GUW/001SN/----20/2 | 1906 |  | 270 | 880 | 88 | None | None | NR 31 |  | 443 | 30 | CHW | 3.78 | 4.06 | 0.93 | 23 | 16.1 | 16 | 15.4 | 0.139 | 7 | 14 | 3.8 | 0 | 0.4 | LPHW | 0.19 | 21 | 21.4 | 0.002 | 80 | 60 | 0.04 |  | 0 | 5.61 | 0.17 | 6 | 1
FCU-20-3031 | FC/H235E/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 51 | None | None | NR 33 |  | 236 | 30 | CHW | 2.21 | 2.41 | 0.92 | 23 | 16.1 | 16 | 14.9 | 0.082 | 7 | 14 | 3.61 | 0 | 0.29 | LPHW | 0.28 | 21 | 22 | 0.003 | 80 | 60 | 0.08 |  | 0 | 6.83 | 0.19 | 3 | 1
FCU-20-3032 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 31 |  | 154 | 30 | CHW | 1.51 | 1.64 | 0.92 | 23 | 16.1 | 16 | 14.5 | 0.056 | 7 | 14 | 2.51 | 0 | 0.19 | LPHW | 0.17 | 21 | 21.9 | 0.002 | 80 | 60 | 0.04 |  | 0 | 5.31 | 0.17 | 2 | 1
FCU-20-3034 | FC/H270H/B4/GUW/001SN/----20/2 | 1591 |  | 270 | 880 | 72 | None | None | NR 32 |  | 366 | 30 | CHW | 3.25 | 3.53 | 0.92 | 23 | 16.1 | 16 | 15.1 | 0.121 | 7 | 14 | 4.42 | 0 | 0.4 | LPHW | 0.38 | 21 | 21.9 | 0.004 | 80 | 60 | 0.08 |  | 0 | 5.97 | 0.18 | 5 | 1
FCU-20-3037 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 206 | 30 | CHW | 1.95 | 2.09 | 0.93 | 23 | 16.1 | 16 | 14.7 | 0.071 | 7 | 14 | 3.23 | 0 | 0.21 | LPHW | 0.1 | 21 | 23 | 0.001 | 80 | 60 | 0.12 |  | 0 | 6.31 | 0.19 | 3 | 1
FCU-20-3038 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 31 |  | 238 | 30 | CHW | 2.16 | 2.19 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.075 | 7 | 14 | 4.1 | 0 | 0.04 | LPHW | 0.35 | 21 | 22.2 | 0.004 | 80 | 60 | 0.09 |  | 0 | 6.06 | 0.2 | 3 | 1
FCU-20-3039 | FC/H270H/B4/GUW/001SN/----20/2 | 1591 |  | 270 | 880 | 72 | None | None | NR 32 |  | 366 | 30 | CHW | 3.25 | 3.53 | 0.92 | 23 | 16.1 | 16 | 15.1 | 0.121 | 7 | 14 | 4.42 | 0 | 0.4 | LPHW | 0.38 | 21 | 21.9 | 0.004 | 80 | 60 | 0.08 |  | 0 | 5.97 | 0.18 | 5 | 1
FCU-20-3040 | FC/H270H/B4/GUW/001SN/----20/2 | 1591 |  | 270 | 880 | 72 | None | None | NR 32 |  | 366 | 30 | CHW | 3.25 | 3.53 | 0.92 | 23 | 16.1 | 16 | 15.1 | 0.121 | 7 | 14 | 4.42 | 0 | 0.4 | LPHW | 0.38 | 21 | 21.9 | 0.004 | 80 | 60 | 0.08 |  | 0 | 5.97 | 0.18 | 5 | 1
FCU-20-3041 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 301 | 30 | CHW | 2.7 | 2.79 | 0.97 | 23 | 16.1 | 16 | 15.1 | 0.095 | 7 | 14 | 3.96 | 0 | 0.14 | LPHW | 0.62 | 21 | 22.7 | 0.007 | 80 | 60 | 0.18 |  | 0 | 5.52 | 0.19 | 4 | 1
FCU-20-3044 | FC/H270H/B4/GUW/001SN/----20/2 | 1591 |  | 270 | 880 | 72 | None | None | NR 32 |  | 366 | 30 | CHW | 3.25 | 3.53 | 0.92 | 23 | 16.1 | 16 | 15.1 | 0.121 | 7 | 14 | 4.42 | 0 | 0.4 | LPHW | 0.38 | 21 | 21.9 | 0.004 | 80 | 60 | 0.08 |  | 0 | 5.97 | 0.18 | 5 | 1
FCU-20-3045 | FC/H270F/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 64 | None | None | NR 32 |  | 301 | 30 | CHW | 2.7 | 2.79 | 0.97 | 23 | 16.1 | 16 | 15.1 | 0.095 | 7 | 14 | 3.96 | 0 | 0.14 | LPHW | 0.62 | 21 | 22.7 | 0.007 | 80 | 60 | 0.18 |  | 0 | 5.52 | 0.19 | 4 | 1
FCU-20-3046 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 200 | 30 | CHW | 1.88 | 2.02 | 0.93 | 23 | 16.1 | 16 | 14.6 | 0.069 | 7 | 14 | 3.11 | 0 | 0.2 | LPHW | 0.4 | 21 | 22.6 | 0.005 | 80 | 60 | 0.09 |  | 0 | 6.2 | 0.19 | 3 | 1
FCU-20-3047 | FC/H235F/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 56 | None | None | NR 32 |  | 240 | 30 | CHW | 2.21 | 2.47 | 0.89 | 23 | 16.1 | 16 | 15 | 0.084 | 7 | 14 | 3.69 | 0 | 0.36 | LPHW | 0.27 | 21 | 21.9 | 0.003 | 80 | 60 | 0.07 |  | 0 | 5.51 | 0.18 | 3 | 1
FCU-20-3048 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 31 |  | 237 | 30 | CHW | 2.14 | 2.17 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.074 | 7 | 14 | 4.07 | 0 | 0.04 | LPHW | 0.13 | 21 | 22.8 | 0.002 | 80 | 60 | 0.13 |  | 0 | 6.05 | 0.2 | 3 | 1
FCU-20-3049 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 33 |  | 200 | 30 | CHW | 1.88 | 2.02 | 0.93 | 23 | 16.1 | 16 | 14.6 | 0.069 | 7 | 14 | 3.11 | 0 | 0.2 | LPHW | 0.4 | 21 | 22.6 | 0.005 | 80 | 60 | 0.09 |  | 0 | 6.2 | 0.19 | 3 | 1
FCU-20-3050 | FC/H270D/B4/GUW/001SN/----20/2 | 961 |  | 270 | 880 | 48 | None | None | NR 30 |  | 226 | 30 | CHW | 2.06 | 2.09 | 0.99 | 23 | 16.1 | 16 | 14.9 | 0.071 | 7 | 14 | 3.91 | 0 | 0.04 | LPHW | 0.1 | 21 | 22.9 | 0.001 | 80 | 60 | 0.13 |  | 0 | 5.9 | 0.19 | 3 | 1
FCU-20-3081 | FC/H235E/B4/GUW/001SN/----20/2 | 1276 |  | 235 | 755 | 51 | None | None | NR 33 |  | 235 | 30 | CHW | 2.19 | 2.4 | 0.91 | 23 | 16.1 | 16 | 14.9 | 0.082 | 7 | 14 | 3.6 | 0 | 0.3 | LPHW | 0.45 | 21 | 22.6 | 0.005 | 80 | 60 | 0.13 |  | 0 | 6.8 | 0.19 | 3 | 1
FCU-30-3001 | FC/H235B/B4/GUW/001SN/----20/2 | 646 |  | 235 | 755 | 31 | None | None | NR 31 |  | 93 | 30 | CHW | 0.99 | 1.02 | 0.97 | 23 | 16.1 | 16 | 13.9 | 0.035 | 7 | 14 | 2.41 | 0 | 0.04 | LPHW | 0.44 | 21 | 24.9 | 0.005 | 80 | 60 | 0.08 |  | 0 | 5.87 | 0.18 | 2 | 1
FCU-30-3002 | FC/H235D/B4/GUW/001SN/----20/2 | 961 |  | 235 | 755 | 43 | None | None | NR 31 |  | 139 | 30 | CHW | 1.19 | 1.32 | 0.9 | 23 | 16.1 | 17.1 | 15.4 | 0.045 | 7 | 14 | 2 | 0 | 0.18 | LPHW | 0.78 | 21 | 25.7 | 0.009 | 80 | 60 | 0.19 |  | 0 | 5.02 | 0.17 | 2 | 1
FCU-30-3007 | FC/H270E/B4/GUW/001SN/----20/2 | 1276 |  | 270 | 880 | 58 | None | None | NR 29 |  | 211 | 30 | CHW | 1.92 | 1.92 | 1 | 23 | 16.1 | 16 | 15.1 | 0.066 | 7 | 14 | 2.7 | 0 | 0 | LPHW | 0.08 | 21 | 21.4 | 0.001 | 80 | 60 | 0.02 |  | 0 | 5.53 | 0.17 | 3 | 1
FCU-30-3008 | FC/H235B/B4/GUW/001SN/----20/2 | 646 |  | 235 | 755 | 31 | None | None | NR 34 |  | 120 | 30 | CHW | 1.22 | 1.24 | 0.98 | 23 | 16.1 | 16 | 14.1 | 0.043 | 7 | 14 | 2.97 | 0 | 0.03 | LPHW | 0.49 | 21 | 24.3 | 0.006 | 80 | 60 | 0.09 |  | 0 | 6.98 | 0.2 | 2 | 1
Project Summary
Sensible Cooling Duty |  |  | 130.50 kW
Total Cooling Duty |  |  | 137.60 kW
Sensible Heat Ratio (SHR) |  |  | 0.9484
Specific Fan Power (SFP) |  |  | 0.19 W/l/s